## Slide 1
Leland Thompson Plant
Hydraulic Reliability
Improvements
Building on recent water quality progress by reducing water hammer and protecting the Atkinson Zone.
August 20, 2026
Notes: Talking points: Open with the big picture: this is not simply a valve replacement. Thompson has become a more complex plant over time, and this project is the next step in protecting both the plant and the Atkinson pressure zone.

## Slide 2
Thompson Plant was built for a simpler job
2012 Original Configuration
The original plant was designed around a much simpler hydraulic path: two supply wells, manganese removal, disinfection, and delivery to the system.
Well 18
Filtronics Vessels
Manganese Removal
Chlorine
Disinfection
Distribution
Atkinson Zone
Original equipment was matched to that original plant.
The valves, pneumatic actuators, vessel controls and programing date back to that simpler operating environment.
130 PSI Operating Range
RCSD | Thompson Plant Hydraulic Reliability Improvements
2
Well 17
Backwash
Tank
Plant Influent Water
Notes: Talking points: Keep this nontechnical. Say: Thompson was built to do one primary job—remove manganese from water supplied by two wells. That is the context the original valves and controls were built around.

## Slide 3
The Plant has evolved over time to meet emerging water quality Regulations
Every improvement helped water quality - but the plant became hydraulically more restrictive.
2012
Thompson built
Manganese treatment around original supply configuration.
2018
Well 2 GAC
Well 2 treatment and blending adds operational dependence.
2019
Well 8A / 1A
Additional source wells become part of the Thompson operating picture.
2021
PFAS IX added
Ion exchange treatment added for PFAS removal.
Today
More complex plant
More piping, valves, instruments, and headloss.
The treatment process improved. The original valve and plant control architecture did not keep pace.
RCSD | Thompson Plant Hydraulic Reliability Improvements
3
Notes: Talking points: Tell the story as modernization, not failure. We have had to add treatment to meet changing water quality requirements. Those additions made the water safer, but also made the plant more complex.

## Slide 4
Thompson Plant 2026 Configuration
Well 18
Filtronics Vessels
Manganese Removal
Chlorine
Disinfection
Distribution
Atkinson Zone
Original equipment is not compatible with today's configuration
170-190 PSI Operating Range
.
RCSD | Thompson Plant Hydraulic Reliability Improvements
4
Well 1A
Well 8
Sodium
Bisulfite
PFAS Pre Filters
Backwash
Tank
Plant Influent Water
Three groundwater sources now operate through the Thompson system: Wells 18, 1A, and 8.
PFAS ion-exchange treatment was added in 2021, including sodium bisulfite feed, cartridge prefilters, additional vessels, piping, valves, and instrumentation.
The added treatment processes created additional flow restriction and headloss, reducing available flow and increasing operating pressure within the plant.
Much of the original valve, actuator, and vessel-control equipment remains from the original plant, even though the hydraulic conditions it operates under have changed substantially.
Notes: Talking points: Keep this nontechnical. Say: Thompson was built to do one primary job—remove manganese from water supplied by two wells. That is the context the original valves and controls were built around.

## Slide 6
256/sec
pressure readings captured
≈30 min
≈100 psi
Pressure Swing felt in
Atkinson Zone
RCSD | Thompson Plant Hydraulic Reliability Improvements
6
Pressure Swings Suring Backwash Cycle
Notes: Talking points: Explain that ordinary SCADA trends can miss very short spikes. These transmitters collect 256 readings per second so we can see the fast pressure events. Emphasize that the swing is felt in the Atkinson pressure zone, not just inside the fence.

## Slide 7
7

## Slide 8
WHY THE PRESSURE SWING MATTERS
Water hammer creates a chain reaction
At Thompson, rapid backwash valve transitions can create pressure waves felt through the Atkinson Zone.
~100 PSI
pressure swing
1
Moving water
Water has momentum
2
Valves move fast
Flow changes suddenly
3
Pressure wave
Energy travels through pipe
4
System stress
Pipes and appurtenances absorb it
5
Mains break
6
Emergency repairs
7
Service interruptions
What absorbs the pressure wave?
Mains • services • meters • hydrants • valves • fittings
Project goal: control valve timing at the source so a backwash transition does not become a system-wide stress event.
RCSD | Thompson Plant Hydraulic Reliability Improvements
8

## Slide 9
COORDINATED MECHANICAL, ELECTRICAL, AND CONTROLS WORK
The Solution: Control The Pressure Event At Its Source
250 psi Pratt valves
Better match current plant pressure conditions
Rotork actuators
Programmable travel speed and position feedback
Zamora electrical
Power and wiring for 15 motorized valves
S-TEK controls
Modern sequencing, SCADA visibility, operator tuning
Goal: smoother backwash transitions, reduced water hammer, and fewer pressure waves through the Atkinson Zone.
RCSD | Thompson Plant Hydraulic Reliability Improvements
9
Current Pneumatic
Valves
Proposed Electric
Rotork Valves
Notes: Talking points: This is where the whole project comes together. The new valves make the hardware fit today’s pressures. The actuators and programming give us control. The electrical work makes it all function. The parallel improvements reduce pressure on the influent side.

## Slide 11
WHY S-TEK IS PART OF THE SOLUTION
The old controls were not built for today’s plant
BEFORE
Original Filtronics control approach
• Original vessel programming
• Pneumatic valve actuation
• Legacy PLC architecture
• Limited control over travel speed
• Less ability to tune backwash transitions
AFTER
S-TEK modern control platform
• New ControlLogix controller
• Programming Rotork actuators on Ethernet/IP
• Updated SCADA graphics
• Programmable valve timing
• Ability to tune backwash sequencing
• New Instrumentation integration
• Complete reprogramming of the
plant's operations
Modern controls allow staff to slow, sequence, and tune the hydraulic transition instead of simply opening and closing valves.
RCSD | Thompson Plant Hydraulic Reliability Improvements
11
Notes: Talking points: Do not spend much time on the PLC model numbers. The simple message: the original system could open and close valves, but the new system gives us the ability to control how fast and in what sequence they move.

## Slide 12
Thompson Plant Hydraulic Reliability Improvements Costs
Project cost
Southwest Valve
$209,563.87
S-TEK
$170,150.00
Zamora Electrical
$46,514.44
10% contingency
$42,622.83
Total authorization
$468,851.14
Funding plan
Line Item 72 – SCADA Replacement
$170,150.00
Water Fund Unrestricted Reserves
$300,000.00
Total project funding
$468,851.14
Board action requested: approve project, authorize agreements, and approve the reserve appropriation for the remaining cost.
12
Notes: Talking points: Close by connecting funding to risk reduction. The full S-TEK amount comes from Line Item 72 because the work is directly SCADA and controls related. The balance requires a reserve appropriation because this was not a standalone budgeted project.

## Slide 13
Recommended Board Actions
Leland Thompson Treatment Plant Valve, Electrical, and Controls Upgrade Project
Approve Project
$469,000
In total not-to-exceed
including 10% contingency and rounding adjustment
2
Add project cost of $469,000 to the FY 26|27 Water Capital Improvement Project Budget
3
Authorize $170,150 from Line Item 72 - SCADA Replacement to fund the Stellar Technology & Automation (S-TEK) portion of the project
$170,150
Line Item 72
Approve a FY 26|27 budget amendment appropriating $298,850 from Water Fund Unrestricted Operating Reserves to fund the remaining project costs.
Authorize GM to Issue Vendor Purchase Orders and Agreements with
5
Southwest Valve & Equipment
$209,563.87
Purchase order for Pratt valves and Rotork actuators.
6
Stellar Technology & Automation
$170,150.00
Agreement for PLC, SCADA, controls, programming, and commissioning.
7
Zamora Industrial Services
$46,514.44
Agreement for electrical improvements and motorized valve connections.
RCSD | Thompson Plant Hydraulic Reliability Improvements
1
4
13